Title
EPICS Database Principles
Andrew Johnson
APS Engineering Support Division
January 2007
USPAS EPICS Course

---
Outline
Outline
Records
Fields and field types
Record Scanning
Input and Output record types
Links, link address types
Connecting records together
Protection mechanisms
Alarms, deadbands, simulation and security

---
Database = Records + Fields + Links
Database = Records + Fields + Links
A control system using EPICS will contain one or more IOCs
Each IOC loads one or more Databases telling it what to do
A Database is a collection of Records of various types
A Record is an object with:
  - A unique name
  - A behavior defined by its record type (class)
  - Controllable properties (fields)
  - Optional associated hardware I/O (device support)
  - Links to other records

---
Record Activity
Record Activity
Records are active — they can do things:
  - Get data from other records or from hardware
  - Perform calculations
  - Check values are in range & raise alarms
  - Put data to other records or to hardware
  - Activate or disable other records
  - Wait for hardware signals (interrupts)
What a record does depends upon its record type and the settings of its fields
No action occurs unless a record is processed

---
How is a Record implemented?
How is a Record implemented?
A ‘C’ structure with a data member for each record field
  - All records start with a standard set of fields (dbCommon) that the system needs, including pointers to record type information
A record definition within a database provides
  - Record name
  - The record’s type
  - Values for each design field
A record type provides
  - Definitions of all the fields
  - Code which implements the record behaviour
New record types can be added to an application as needed

---
One view of a Record
One view of a Record

---
A graphical view of a Record
A graphical view of a Record

---
Another graphical view of a Record
Another graphical view of a Record
The small CapFast symbol for an Analogue Output record

---
The IOC’s view
The IOC’s view
The full .db file entry for an Analogue Output Record
record(ao,"DemandTemp") {
field(DESC,"Temperature")
field(ASG,"")
field(SCAN,"Passive")
field(PINI,"NO")
field(PHAS,"0")
field(EVNT,"0")
field(DTYP,"VMIC 4100")
field(DISV,"1")
field(SDIS,"")
field(DISS,"NO_ALARM")
field(PRIO,"LOW")
field(FLNK,"")
field(OUT,"#C0 S0")
field(OROC,"0.0e+00")
field(DOL,"")
field(OMSL,"supervisory")
field(HHSV,"NO_ALARM")
field(LLSV,"NO_ALARM")
field(HSV,"NO_ALARM")
field(LSV,"NO_ALARM")
field(HYST,"0.0e+00")
field(ADEL,"0.0e+00")
field(MDEL,"0.0e+00")
field(SIOL,"")
field(SIML,"")
field(SIMS,"NO_ALARM")
field(IVOA,"Continue normally")
field(IVOV,"0.0e+00")
}
This shows only the design fields; there are other fields which are used only at run-time
  field(OIF,"Full")
  field(PREC,"1")
  field(LINR,"NO CONVERSION")
  field(EGUF,"100")
  field(EGUL,"0")
  field(EGU,"Celcius")
  field(DRVH,"100")
  field(DRVL,"0")
  field(HOPR,"80")
  field(LOPR,"10")
  field(HIHI,"0.0e+00")
  field(LOLO,"0.0e+00")
  field(HIGH,"0.0e+00")
  field(LOW,"0.0e+00")

---
Fields are for...
Fields are for...
Defining
  - What causes a record to process
  - Where to get/put data from/to
  - How to turn raw I/O data into a numeric engineering value
  - Limits indicating when to report an alarm
  - When to notify value changes to a client monitoring the record
  - A Processing algorithm
  - Anything else which needs to be set for each record of a given type
Holding run-time data
  - Input or output values
  - Alarm status, severity and acknowledgments
  - Processing timestamp
  - Other data for internal use

---
Field types
Field types — fields can contain:
Integers
  - char, short or long
  - signed or unsigned
Floating-point numbers
  - float or double
Fixed length strings
  - maximum useful length is 40 characters
Enumerated/menu choices
  - select one of up to 16 strings
  - stored as a short integer
Arrays of any of the above types
Links
  - to other records in this or other IOCs
  - to hardware signals (device support)
  - provide a means of getting or putting a value
Other private data
  - not accessible remotely

---
All Records have these fields
All Records have these design fields
NAME	60 Character unique name (using more than 28 can cause problems)
DESC	28 Character description
ASG	Access security group
SCAN	Scan mechanism
PHAS	Scan order (phase)
PINI	Process at IOC initialization?
PRIO	Scheduling priority
SDIS	Scan disable input link
DISV	Scan disable value
DISS	Disabled severity
FLNK	Forward link

---
All Records have Run-time fields
All Records have these Run-time fields
PROC	Force processing
PACT	Process active
STAT	Alarm status
SEVR	Alarm severity
TPRO	Trace processing
UDF	Non-zero if record value undefined
TIME	Time when record was last processed

---
Record Scanning
Record Scanning
SCAN field is a menu choice from
  - Periodic — 0.1 seconds .. 10 seconds
  - I/O Interrupt (if device supports this)
  - Soft event — EVNT field
  - Passive (default)
The number in the PHAS field allows processing order to be set within a scan
  - Records with PHAS=0 are processed first
  - Then those with PHAS=1 , PHAS=2 etc.
Records with PINI=YES are processed once at startup
PRIO field selects Low/Medium/High priority for Soft event and I/O Interrupts
A record is also processed whenever any value is written to its PROC field

---
Input records often have these fields
Input records often have these fields
INP	Input link
DTYP	Device type
RVAL	Raw data value
VAL	Engineering value
LOPR	Low operator range
HOPR	High operator range

---
Analog I/O fields
Analogue I/O records have these fields:
EGU	Engineering unit string
LINR	Unit conversion control: No conversion, Linear, Slope,
        breakpoint table name
EGUL	Low engineering value
EGUF	High engineering value
ESLO	Unit conversion slope
EOFF	Unit conversion offset

---
Periodic Input
Periodically Scanned Analog Input
Analogue Input “Temperature”
Reads from the Xycom XY566 ADC Card 0 Signal 0
Gets a new value every second
Data is converted from ADC range to 0..120 Celsius

---
Interrupt Input
Interrupt Scanned Binary Input
Binary Input “VentValve”
Reads from Allen-Bradley TTL I/O Link 0, Adaptor 0, Card 3, Signal 5
Processed whenever value changes
0 = “Closed”, 1 = “Open”
Major alarm when valve open

---
Output records often have these fields
Most output records have these fields
OUT	Output link
DTYP	Device type
VAL	Engineering value
RVAL	Raw output value
DOL	Input link to fetch output value
OMSL	Output mode select:
      - Supervisory, Closed Loop
LOPR	Low operator range
HOPR	High operator range

---
Analog Output fields
Analogue outputs also have these fields:
OROC	Output rate of change
OIF	Incremental or Full output
OVAL	Output value
DRVH	Drive high limit
DRVL	Drive low limit
IVOA	Invalid output action
IVOV	Invalid output value
RBV	Read-back value

---
Passive Output
Passive Binary Output
Binary Output “Solenoid”
Controls Xycom XY220 Digital output Card 2 Signal 12
Record is only processed by
  - Channel Access ‘put’ to a PP field (e.g. .VAL)
  - Another record writes to a PP field
  - Forward Link from another record
  - Another record reads this with PP

---
Break #1
Break time...
5 Minute break

---
Links
Links
A link is a type of field, and is one of
Input link
  - Fetches data
Output link
  - Writes data
Forward link
  - Points to the record to be processed once this record finishes processing

---
Input and Output links may be...
Input and Output links may be...
Constant numeric value, e.g.:
  - 0
  - 3.1415926536
  - -1.6e-19
Hardware link
  - A hardware I/O signal selector, the format of which depends on the device support layer
Process Variable link — the name of a record, which at run-time is resolved into
  - Database link
    - Named record is in this IOC
  - Channel Access link
    - Named record not found in this IOC

---
Hardware links
Hardware links
VME_IO	#Cn Sn @parm
      - Card, Signal
INST_IO	@parm
CAMAC_IO	#Bn Cn Nn An Fn @parm
      - Branch, Crate, Node, Address, Function
AB_IO	#Ln An Cn Sn @parm
      - Link, Adapter, Card, Signal
GPIB_IO	#Ln An @parm
      - Link, Address
BITBUS_IO	#Ln Nn Pn Sn @parm
      - Link, Node, Port, Signal
BBGPIB_IO	#Ln Bn Gn @parm
      - Link, Bitbus Address, GPIB Address
VXI_IO	#Vn Cn Sn @parm
or	#Vn Sn @parm
      - Frame, Slot, Signal

---
Database links
Database links
These comprise:
  - The name of a record in this IOC
    - myDb:myRecord
  - An optional field name
    - .VAL (default)
  - Process Passive flag
    - NPP (default), or PP
  - Maximize Severity flag
    - NMS (default), or MS
For example:
  - M1:current.RBV NPP MS
NB: An input database link with the PP flag set that is pointing to an asynchronous input record will not wait for the new value from that record

---
Channel Access links
Channel Access links
Specified like a database link
Name specifies a record not found in this IOC
Use Channel Access protocol to communicate with remote IOC
May include a field name (default .VAL)
PP Link flags are ignored:
  - Input links are always NPP
  - Output links follow PP attribute of destination field
  - This behavior is identical to all other CA clients
MS Link flags apply to Input links:
  - Input links honor a given NMS (default) or MS flag
  - Output links are always NMS
Additional flags for CA links:
  - CA	Forces a “local” link to use CA
  - CP	On input link, process this record on CA monitor event
  - CPP	Like CP but only process if SCAN is Process Passive

---
Link flag summary
Link flag summary
Chapter 5 of the IOC Application Developer’s Guide covers
record links and scanning in detail, and is worth reading.

---
Device Support
Device Support
Records do not access hardware directly
The Device Support layer performs I/O operations on request
A particular device support provides I/O for a single record type
The DTYP field determines which device support to use
The device support selected determines the format of the link (INP or OUT field) containing device address information
Adding new device support does not require change to the record software
Device support may call other software to do work for it (Driver Support)

---
Synchronous vs Asynchronous I/O
Synchronous vs Asynchronous I/O
EPICS rules do not allow device support to busy-wait (i.e. delay record processing while waiting for the results of a slow I/O operation)
  - Fast I/O can be handled synchronously
  - Slow operations must operate asynchronously
Register-based VME cards usually give an immediate response: synchronous
When called, synchronous device support performs all I/O before returning
Serial and field-bus I/O takes a long time (>10ms) to return data: asynchronous
Asynchronous device support starts an I/O operation when the record calls it, flagging it as incomplete by setting PACT to true before returning
Once results are available (CPU interrupt), the device support calls the record’s process() routine to finish the record processing operations

---
Soft Device Support
Soft Device Support
“Hard” Input and Output records perform hardware I/O via device support
“Soft” records access data from other records via DB or CA links
2 or 3 kinds of support are provided in recent R3.14 releases:
  - Soft Channel
    - Get/Put VAL through link, no units conversion preformed
  - Async Soft Channel (new, for output records only)
    - Put VAL through CA link, no conversions, wait for completion
  - Raw Soft Channel
    - Inputs
      - Get RVAL via input link
      - Convert RVAL to VAL (record-type specific)
    - Outputs
      - Convert VAL to RVAL (record-type specific)
      - Put RVAL to output link

---
Forward links
Forward links
Usually a Database link, referring to a record in same IOC
No flags (PP, MS etc.), although VDCT includes them erroneously
Destination record is only processed if its SCAN field is Passive
Does not pass a value, just causes subsequent processing
Forward linking to another IOC via Channel Access is possible, but the link must explicitly name the PROC field of the remote record
  - In this case, the remote record does not have to be SCAN Passive

---
Processing chains
Processing chains

---
Which record is never processed?
Which record is never processed?

---
How often is Input_1 processed?
How often is Input_1 processed?

---
The PACT field
The PACT field
Every record has a boolean run-time field called PACT (Process Active)
PACT breaks loops of linked records
It is set to true early in the act of processing the record (but it's not the first thing that the process routine does)
  - PACT is true whenever a link in that record is used to get/put a value
PACT is set to false after record I/O and forward link processing are finished
A PP link can never make a record process if it has PACT true
  - Input links take the current value
  - Output links just put their value

---
What happens here?
What happens here?

---
Preventing records from processing
Preventing records from processing
It is useful to be able to stop an individual record from processing on some condition
Before record-specific processing is called, a value is read through the SDIS input link into DISA (which defaults to 0 if the link is not set)
If DISA=DISV, the record will not be processed
The default value of the DISV field is 1
A disabled record may be put into an alarm state by giving the desired severity in the DISS field
The FLNK of a disabled record is never triggered

---
Break #2
Break time...
5 Minute break

---
Order of Operations (Sync) #1
Order of Operations (Synchronous I/O)
Every 0.1 seconds, iocCore will attempt to process the Output_1 record
The Output_1.PACT field is currently False, so the record is quiescent and can be processed
If set, the Output_1.SDIS link would be read into Output_1.DISA
Since DISA≠DISV, the ao record type's process() routine is called

---
Order of Operations (Sync) #2
Order of Operations (Synchronous I/O)
The ao's process() routine checks the Output_1.OMSL field; it is closed_loop, so
It sets Output_1.PACT to True, then
Reads a value through the Output_1.DOL link
The Output_1.DOL link contains Calculation_1.VAL PP so this first attempts to process the Calculation_1 record

---
Order of Operations (Sync) #3
Order of Operations (Synchronous I/O)
The Calculation_1.SCAN field is Passive and Calculation_1.PACT is False, so processing is possible
If set, the Calculation_1.SDIS link would be read into DISA
Since DISA≠DISV, the calc record type's process() routine is called

---
Order of Operations (Sync) #4
Order of Operations (Synchronous I/O)
The calc's process() routine sets Calculation_1.PACT to True, then
Starts a loop to read values from the links INPA through INPL
The Calculation_1.INPA link is set to Input_1.VAL PP so this first attempts to process the Input_1 record

---
Order of Operations (Sync) #5
Order of Operations (Synchronous I/O)
The Input_1.SCAN field is Passive and Input_1.PACT is False, so processing is possible
If set, the Input_1.SDIS link is read into the Input_1.DISA field
Since DISA≠DISV, the ai record type's process() routine is called
The ai process() calls the associated device support to read a value from the hardware it's attached to

---
Order of Operations (Sync) #6
Order of Operations (Synchronous I/O)
The device support is synchronous, so it puts the hardware input value into the Input_1.RVAL field and returns to the ai record's process() code
The Input_1.PACT field is set to True
The record's timestamp field Input_1.TIME is set to the current time
The raw value in Input_1.RVAL is converted to engineering units, smoothed, and the result put into the Input_1.VAL field

---
Order of Operations (Sync) #7
Order of Operations (Synchronous I/O)
The Input_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate actions is taken if these are exceeded
If the Forward Link field Input_1.FLNK is set, an attempt is made to process the record it points to
The Input_1.PACT field is set to False, and the process() routine returns control to the Calculation_1 record

---
Order of Operations (Sync) #8
Order of Operations (Synchronous I/O)
The value read through the Calculation_1.INPA link is copied into the Calculation_1.A field
The Calculation record type's process() routine continues to loop, reading its input links
In this example only the INPA link is set, so the routine finishes the loop and evaluates the Calculation_1.CALC expression (not shown)
The result of the expression is put in the Calculation_1.VAL field

---
Order of Operations (Sync) #9
Order of Operations (Synchronous I/O)
The record's timestamp field Calculation_1.TIME is set to the current time
Calculation_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate action is taken if these are exceeded
If the Forward Link field Calculation_1.FLNK is set, an attempt is made to process the record it points to
The Calculation_1.PACT field is set to False, and the process() routine returns control to the Output_1 record

---
Order of Operations (Sync) #10
Order of Operations (Synchronous I/O)
The value read through the Output_1.DOL link would now be forced into the range DRVL..DRVH if those fields were set, but they aren't so it's copied to the Output_1.VAL field unchanged
The Output_1.VAL value is converted from engineering to raw units and placed in Output_1.RVAL
Output_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate action is taken if these are exceeded
The associated device support is called to write the value to the hardware

---
Order of Operations (Sync) #11
Order of Operations (Synchronous I/O)
The device support is synchronous, so it outputs the value to the attached hardware and returns
The record's timestamp field Output_1.TIME is set to the current time
If the Forward Link field Output_1.FLNK is set, an attempt is made to process the record it points to
The Output_1.PACT field is set to False, and the process() routine returns

---
How are records given CPU time?
How are records given CPU time?
Several IOC tasks are used:
callback (3 priorities) — I/O Interrupt
scanEvent — Soft Event
scanPeriod — Periodic
  - A separate task is used for each scan period
  - Faster scan rates are given a higher task priority (if supported by the IOC’s Operating System)
Channel Access tasks use lower priority than record processing
  - If a CPU spends all its time doing I/O and record processing, you may be unable to control or monitor the IOC via the network

---
What could go wrong here?
What could go wrong here?

---
Lock-sets
Lock-sets
Prevent a record from being processed simultaneously from two scan tasks
A lock-set is a group of records interconnected by database links:
  - Output links
  - Forward links
  - Input links which are PP or MS
  - Any link transporting an Array
Lock-sets are determined automatically by the IOC at start-up, or whenever a database link is added, deleted or modified
You can split a lock set with
Channel Access links, using CA flag
Database links which are both NPP and NMS

---
Alarms
Alarms
Every record has the fields
  - SEVR	Alarm Severity
    - NONE, MINOR, MAJOR, INVALID
  - STAT	Alarm Status (reason)
    - READ, WRITE, UDF, HIGH, LOW, STATE, COS, CALC, DISABLE, etc.
Most numeric records check VAL against HIHI, HIGH, LOW and LOLO fields after the value has been determined
The HYST field prevents alarm chattering
A separate severity can be set for each numeric limit (HHSV, HSV, LSV, LLSV)
Discrete (binary) records can raise alarms on entering a particular state, or on a change of state (COS)

---
Change Notification: Monitor Deadbands
Change Notification: Monitor Dead-bands
Channel Access notifies clients that are monitoring a numeric record when
  - VAL changes by more than the value in field:
    - MDEL	Value monitors
    - ADEL	Archive monitors
  - Record’s Alarm Status changes
    - HYST	Alarm hysteresis
The Analogue Input record provides a smoothing filter to reduce noise on the input signal (SMOO)

---
Breakpoint Tables
Breakpoint Tables
Type J Thermocouple
Raw Input, ADC Units
Engineering Value, Celcius
Analogue Input and Output records can do non-linear conversions from/to the raw hardware value
Breakpoint tables interpolate values from a given table
To use, set the record’s LINR field to the name of the breakpoint table you want to use
Example breakpoint table (in some loaded .dbd file)
  - breaktable(typeKdegC) {
  - 0.000000 0.000000
  - 299.268700 74.000000
  - 660.752744 163.000000
  - 1104.793671 274.000000
  - 1702.338802 418.000000
  - 2902.787322 703.000000
  - 3427.599045 831.000000
  - ...
  - }

---
Simulation
Simulation
Input and output record types often allow simulation of hardware interfaces
  - SIML	Simulation mode link
  - SIMM	Simulation mode value
  - SIOL	Simulation input link
  - SIMS	Simulation alarm severity
Before using its device support, a record reads SIMM through the SIML link
If SIMM=YES, device support is ignored; record I/O uses the SIOL link instead
An alarm severity can be set whenever simulating, given by SIMS field

---
Access Security
Access Security
A networked control system must have the ability to enforce security rules
  - Who can do what from where, and when?
In EPICS, security is enforced by the CA server (typically the IOC).
A record is placed in the Access Security Group named in its ASG field
  - DEFAULT is used if no group name is given
Rules for each group determine whether a CA client can read or write to records in the group, based on
  - Client user ID
  - Client IP address
  - Access Security Level of the field addressed
  - Values read from the database

---
Access Security Configuration File
Access Security Configuration File
Security rules are loaded from an Access Security Configuration File, for example:
  - UAG(users) {user1, user2}
  - HAG(hosts) {host1, host2}
  - ASG(DEFAULT) {
  - RULE(1, READ)
  - RULE(1, WRITE) {
  - UAG(users)
  - HAG(hosts)
  - }
  - }
If no security file is loaded, Security will be turned off and nothing refused
For more details and the rule syntax, see Chapter 8 of the IOC Application Developers Guide