PowerPoint Presentation
EPICS Database Practice
Andrew Johnson
APS Engineering Support Division
June 2010
USPAS EPICS Course

---
EPICS record types
- Where do record types come from?
  - EPICS Base (<base>/src/rec)
    - General purpose record types
    - No record-type specific operator displays or databases
    - Documentation in the EPICS Record Reference Manual
  - EPICS collaboration
    - General purpose, and application-specific, record types
    - Some are supported for use by collaborators (some are NOT)
    - Some come with record-type specific displays and database templates
  - Custom record types can be written by any EPICS developer, and added to specific EPICS applications as needed.
    - Not in the scope of this lecture

---
The Record Reference Manual
- Where is it?
  - EPICS Home > Base > R3.14.11 > Reference Reference Manual (wiki)
- What is in it?
  - Database Concepts (good review)
  - Fields common to all records (covered earlier)
  - Fields common to many records (covered earlier)
  - Record Types – provides a description of the fields and record processing routines for the record types in base.
- When would I use it?
  - Skim through before writing any databases
  - Read through before writing any records
  - Otherwise, use as reference

---
Manual Outline
- Preface, Chapter 1: Essential background information
  - Note special meaning of the words scan, process, address, link, and monitor
- Chapter 2-39: Record reference
  - Some parts may still be slightly out of date
  - Descriptions of record fields, processing, and useful info for writing device support
  - Contains lots of tables like this:
No
No
Yes
Yes
Null
Yes
STRING [29]
Description
DESC
No
No
No
Yes
Null
Yes
STRING [29]
Record Name
NAME
No
No
Yes
Yes
0
Yes
SHORT
Display Precision
PREC
No
No
Yes
Yes
0
Yes
FLOAT
Low Operating Range
LOPR
No
No
Yes
Yes
0
Yes
FLOAT
High Operating Range
HOPR
No
No
Yes
Yes
null
Yes
STRING [16]
Engineering Units
EGU
PP
Rec Proc Monitor
Modify
Access
Initial
DCT
Type
Summary
Field

---
Collaboration supported records
- Where are they found?
  - Soft-support list: http://www.aps.anl.gov/epics/modules/soft.php
  - The tech-talk email list
  - The soft-support list contains entries like this (among entries for other kinds of soft support):
SLAC:time stamp
Stephanie Allison
...exports its timestamp as a string
timestamp
record
APS:synApps/optics
Tim Mooney
Control an optical table
table
record
...
...
...
...
...
OSL:epics
Andy Foster
Multi-I/O subroutine, handles arrays
genSub
record
CARS:epid Record
Enhanced PID record
epid
record
Link
Contact
Description
Name
Class
Mark Rivers

---
Input Records
- ai - Analog input [BASE]
  - Read analog value, convert to engineering units, four alarm levels, simulation mode
- aai – Array analog input [BASE]
  - Read array of analog values, simulation mode
- bi - Binary input [BASE]
  - Single bit, two states, assign strings to each state, alarm on either state or change of state, simulation mode
- mbbi - Multi-bit binary input [BASE]
  - Multiple bit, sixteen states, assign input value for each state, assign strings to each state, assign alarm level to each state, simulation mode
- mbbiDirect – mbbi variant [BASE]
  - Read an unsigned short and map each bit to a field (16 BI records in one)

---
Input Records (cont..)
- stringin - String input [BASE]
  - 40 character (max) ascii string, simulation mode
- longin - Long integer input [BASE]
  - Long integer, four alarm levels, simulation mode
- waveform – array input [BASE]
  - Configurable data type and array length (16,000 bytes max for CA in EPICS 3.13)
- mbbi32Direct [ORNL] longMbbiDirect [KEK] – 32-bit mbbiDirect
  - Read an unsigned long and map each bit to a field (32 BI records in one)
- mca – multichannel analyzer [synApps]
  - Supports multichannel analyzers, multichannel scalers, and other array-input hardware

---
Input Records (cont..)
- pulseCounter [ANL RecRefMan]
  - Written to support a Mizar 8310 timing module
- scaler [synApps]
  - Controls a bank of counters
- swf [BESSY] , wftime [SLAC] – waveform variants
  - Includes scaling and time (wftime) information
- timestamp [SLAC]
  - Exports its timestamp as a string
  - No longer needed, use stringin record with timestamp device support

---
Algorithms/Control Records - Calc
- calc - run-time expression evaluation [BASE]
  - 12 input links, user specified expression (algebraic, trig, relational, boolean, bit-wise, “?:” and “:=” operators), four alarm levels
  - Sample expressions:
    - 0 read: “VAL = 0”
    - A returns value of record’s “A” field
    - A+B
    - b*sin(a*d2r); a:=a+1
    - (A+B)<(C+D) ? E : F*G/100
- calcout – calc variant [BASE]
  - Conditional output link, second output CALC expression (.OCAL), output delay, and output event
  - Output-link options : "Every Time”, "On Change", "When Zero", "When Non-zero", "Transition To Zero", "Transition To Non-zero“

---
Algorithms/Control Records - Calc
- sCalcout – calcout variant [synApps]
  - Has both numeric fields (A,B,..L) and string fields (AA,BB,..LL)
  - Supports both numeric and string expressions. E.g.,
    - A+DBL(“value is 3.456”) -> 4.456
    - printf(“SET:VOLT:%.2lf”, A+4) -> “SET:VOLT:5.00”
  - Additional output-link option: “Never”
- transform – calc/seq variant [synApps]
  - Like 16 calcout records (but outlinks are not conditional)
  - Expressions read all variables, but write to just one.
  - Uses sCalcout record’s calculation engine
  - Example expressions:
    - A: 2 read: “<transform>.A = 2”
    - B: A+1+C uses new value of ‘A’, old value of ‘C’

---
Algorithms/Control Records - Array
- compress [BASE]
  - Input link can be scalar or array.
  - Algorithms include N to 1 compression (highest, lowest, or average), circular buffer of scalar input.
- histogram [BASE]
  - Accumulates histogram of the values of a scalar PV
- subArray [BASE]
  - Extracts a sub-array from a waveform.
- aConcat [KEK], joinArray [SLS]
  - Concatenate waveforms
- aSub – sub variant [BASE], genSub [OSL]
  - Multiple inputs and outputs
  - Handles arrays

---
Algorithms/Control Records – List
- dfanout – Data fanout [BASE]
  - Writes a single value to eight output links
- fanout [BASE]
  - Forward links to six other records.
  - Selection mask
- sel - Select [BASE]
  - 12 input links, four select options [specified, highest, lowest, median], four alarm levels
- seq - Sequence [BASE]
  - Ten “Input link/Value/Output link” sets: [inlink, delay, value, outlink]
  - Selection mask

---
Algorithms/Control Records – List
- lseq – seq variant [JACH]
  - 16 sets, instead of 10
- sseq – seq variant [synApps]
  - seq record for string or numeric data
  - optional wait for completion after each set executes
wfselector – waveform/sel variant [KEK]
- aSub [BASE]
- genSub [OSL]
- sCalcout [synApps]
- transform [synApps]

---
Algorithms/Control Records - Loop
- scan [synApps]
  - Four “positioners”, two “detector triggers”, fifteen “detectors”.
  - Systematically sets conditions, triggers detectors, and acquires data into arrays.
  - Database detects completion and drives scan to next step.
- sscan – scan variant [synApps]
  - Uses ca_put_callback() to detect completion.
  - Four triggers, 70 detector signals (arrays, scalars, or mixed)
  - Array-prepare trigger at end of scan
  - Number of data points stored is limited only by memory
  - Supports scan pause; before/after-scan action; move-to-peak.
  - Handshake permits data-storage client to write old data while new data is being acquired.

---
Algorithms/Control Records - Subroutine
- sub – Subroutine [BASE]
  - 12 input links, user provided subroutine, four alarm levels
- aSub – Array Subroutine [BASE]
  - 21 input links, 21 output links, controllable data types and array sizes
  - user provided initialize and process subroutines
- genSub – original aSub variant [OSL]
  - Also handles structures

---
Algorithms/Control Records - Other
- event [BASE]
  - Posts a “soft” event which may trigger other records to process.
  - Simulation mode
- PID [ANL], CPID [JLAB], EPID [synApps]
  - Proportional/Integral/Derivative Control
- pal [3.13 BASE]
  - Emulates Programmable Array Logic
- cvt – ai/ao variant [BESSY]
  - 1 or 2 inputs, 1 output, conversion types: linear, subroutine, 1D or 2D table
- Permissive – handshake [BASE]
  - Implements a client-server handshake
- state – string state value [BASE]
  - Implements a string, for client-server communication

---
Output Records
- ao - Analog output [BASE]
  - Write analog value, convert from engineering units, four alarm levels, closed_loop mode, drive limits, output rate-of-change limit, INVALID alarm action, simulation mode
- aao – Array analog output [BASE]
  - ao for arrays
- bo - Binary output [BASE]
  - Single bit, two states, assign strings to each state, alarm on either state or change of state, closed_loop mode, momentary ‘HIGH’, INVALID alarm action, simulation mode
- longout [BASE]
  - Write long integer value, four alarm levels, closed_loop mode, INVALID alarm action, simulation mode

---
Output Records (cont..)
- mbbo - Multi-bit binary output [BASE]
  - Multiple bit, sixteen states, assign output value for each state, assign strings to each state, assign alarm level to each state, closed_loop mode, INVALID alarm action, simulation mode
- mbboDirect - mbbo variant [BASE]
  - 16 settable bit fields that get written as a short integer to the hardware, closed_loop mode, INVALID alarm action, sim. mode
- mbbo32Direct - mbbo variant [ORNL]
- longMbboDirect - mbbo variant [KEK]
  - 16 settable bit fields that get written as a long integer, closed_loop mode, INVALID alarm action, simulation mode
- motor [synApps]
  - Controls stepper and servo motors
  - Has its own lecture (Motors)

---
Output Records (cont..)
- steppermotor [3.13 BASE]
  - Position control, retry, speed, ramps, etc
- pulseDelay [3.13 BASE]
  - Written to support a Mizar 8310 timing module
- pulseTrain [3.13 BASE]
  - Written to support a Mizar 8310 timing module
- stringout [BASE]
  - Write a character string (40 max), closed_loop mode, INVALID alarm action, simulation mode

---
Examples of Custom Records
- rf - RF Amplitude Measurements [ANL]
  - Sample time, measurement in watts and db, waveform acquired through sweeping sample time
- bpm - Beam Position Monitor [ANL]
  - Four voltage inputs, numerous calibration constants, X-Y-I outputs, waveforms for each input
- Many others that are site-specific

---
Which record is right for …
- Soft parameters entered by an operator
  - AO has DRVH, DRVL, OROC, closed loop
  - MBBO provides enumerated options which can be converted to constants (use DTYP = Raw Soft Channel)
  - Normally one does not use input records for this purpose
- Multiple output actions
  - Sequence record can have a different data source for each output link vs. the dfanout record which “fans out” a single source to multiple links
- Different output actions based on an operator selection
  - CALCOUT records that conditionally process sequence records
  - MBBO (Soft Raw Channel) forward linked to a single sequence record in “masked” mode. Mask is provided in MBBO for each state.

---
Defining the Database
- How does an IOC know what record types and device support options are available ?
  - Record types, device support options, choice menus, and other configuration options are defined in Database Definition files (.dbd)
  - The IOC build process creates a .dbd file containing everything the IOC needs
  - That .dbd file is loaded by the IOC when it starts up
- How does an IOC know about record instances (the user’s database) ?
  - Record instances are describe in Database files (.db)
  - During the IOC booting process, one or more .db files are loaded
  - The .db files define the record instances for that IOC

---
Database Definition File
menu(menuPriority) {
  choice(menuPriorityLOW,"LOW")
  choice(menuPriorityMEDIUM,"MEDIUM")
  choice(menuPriorityHIGH,"HIGH")
}
menu(menuScan) {
  choice(menuScanPassive,"Passive")
  choice(menuScanEvent,"Event")
  choice(menuScanI_O_Intr,"I/O Intr")
  choice(menuScan10_second,"10 second")
  choice(menuScan5_second,"5 second")
  choice(menuScan2_second,"2 second")
  choice(menuScan1_second,"1 second")
  choice(menuScan_5_second,".5 second")
  choice(menuScan_2_second,".2 second")
  choice(menuScan_1_second,".1 second")
}
device(ai,CONSTANT,devAiSoftRaw,
        "Raw Soft Channel")
device(ai,BITBUS_IO,devAiIObug,
        "Bitbus Device")
device(ao,CONSTANT,devAoSoftRaw,
        "Raw Soft Channel")
device(ao,VME_IO,devAoAt5Vxi,
        "VXI-AT5-AO")
device(bi,VME_IO,devBiAvme9440,
        "AVME9440 I")
device(bi,AB_IO,devBiAb,
        "AB-Binary Input")
driver(drvVxi)
driver(drvMxi)
driver(drvGpib)
driver(drvBitBus)
Extracts from a typical .dbd file

---
Database Definition File continued...
menu(aoOIF) {
 choice(aoOIF_Full,"Full")
 choice(aoOIF_Incremental,
        "Incremental")
}
recordtype(ao) {
  include "dbCommon.dbd"
  field(VAL,DBF_DOUBLE) {
    prompt("Desired Output")
    promptgroup(GUI_OUTPUT)
    asl(ASL0)
    pp(TRUE)
  }
  field(OUT,DBF_OUTLINK) {
   prompt("Output Specification")
   promptgroup(GUI_OUTPUT)
   interest(1)
 }
  field(OIF,DBF_MENU) {
   prompt("Out Full/Incremental")
   promptgroup(GUI_OUTPUT)
   interest(1)
   menu(aoOIF)
  }
 field(OVAL,DBF_DOUBLE) {
    prompt("Output Value")
  }
 field(PREC,DBF_SHORT) {
   prompt("Display Precision")
   promptgroup(GUI_DISPLAY)
   interest(1)
 }
 ...
}
Parts of the ao record type definition from a typical .dbd file

---
Database File
record(bo,"$(user):gunOnC") {
    field(DESC,"Controls e-gun")
}
record(bo,"$(user):gunOnC") {
    field(DESC,"Controls e-gun")
    field(DTYP,"Soft Channel")
    field(ZNAM,"Beam Off")
    field(ONAM,"Beam On")
}
record(ao,"$(user):cathodeCurrentC") {
    field(DESC,"set cathode current")
    field(DTYP,"Raw Soft Channel")
    field(SCAN,"1 second")
    field(OROC,".5")
    field(PREC,"2")
    field(EGU,"Amps")
    field(DRVH,"20")
    field(DRVL,"0")
    field(HOPR,"20")
    field(LOPR,"0")
}
record(calc,"$(user):rampM") {
    field(CALC,"A>6.27?0:A+.1")
    field(SCAN,"1 second")
    field(INPA,"$(user):rampM.VAL")
}
record(calc,"$(user):cathodeTempM") {
    field(DESC,"Measured Temp")
    field(SCAN,"1 second")
    field(CALC,"C+(A*7)+(SIN(B)*3.5)")
    field(INPA,"$(user):cathodeCurrentC.OVAL")
    field(INPB,"$(user):rampM.VAL")
    field(INPC,"70")
    field(EGU,"degF")
    field(PREC,"1")
    field(HOPR,"200")
    field(LOPR,"")
    field(HIHI,"180")
    field(LOLO,"130")
    field(HIGH,"160")
    field(LOW,"140")
    field(HHSV,"MAJOR")
    field(HSV,"MINOR")
    field(LLSV,"MAJOR")
    field(LSV,"MINOR")
}

---
Loading Database Files into the IOC
A typical startup script (st.cmd) might contain
dbLoadDatabase("../../dbd/linacApp.dbd")
dbLoadRecords("../../db/xxLinacSim.db","user=studnt1")
iocInit /* starts database processing */
- One or more database definition files (.dbd) must be loaded first.
  - Any record type used in the database files must have been defined in the definition file
- Values for macros used within the database file (e.g. $(user) ) can be specified when loading. This allows a database to be loaded more than once with different record names and I/O addresses each time

---
Creating Database Files
- Since the database file is a simple ascii file, it can be generated by numerous applications … as long as the syntax is correct
  - Text editor
  - Script (Perl, Python, shell, awk, sed, …)
  - Relational Database (Oracle, MySQL)
  - EPICS-aware Database Configuration Tools:
    - VDCT (recommended for new designs)
    - CAPFAST (a schematic entry application)
    - JDCT (not graphical)
- An EPICS-aware tool will read the IOC’s .dbd file for menu selections of enumerated fields. It may also detect database errors prior to the boot process
- A hierarchical graphical tool is helpful for complex databases

---
Database Examples
Calculating “Rate-of-Change” of an Input
INPA fetches data that is 1 second old because it does not request processing of the AI record. INPB fetches current data because it requests the AI record to process. The subtraction of these two values reflects the ‘rate of change’ (difference/sec) of the pressure reading.

---
Database Examples
When in simulation mode, the AO record does not call device support and the AI record fetches its input from the AO record.

---
Database Examples
Maximize Severity
If chassis is powered off, Temp Trip and Flow Trip indicate Normal. Force these PVs into an alarm state by specifying .SDIS with .MS (maximize severity) to the Chassis On record. Set .DISV (disable value) to 2 so processing will never be disabled.

---
Database Examples
Slow Periodic Scan with Fast Change Response
The AI record gets processed every 5 seconds AND whenever the AO record is changed. This provides immediate response to an operator's changes even though the normal scan rate is very slow. Changes to the power supply settings are inhibited by the BO record, which represents a Local/Remote switch.

---
Database Examples
Different Actions Based on Operator Selection
record(mbbo,"$(user):PS:Control") {
        field(DTYP,"Raw Soft Channel")
        field(FLNK,"$(user):PS:ControlSQ.VAL PP NMS")
        field(ZRVL,”0x3") BIT MAP: 0000000000000011 -> do LNK1, LNK2
        field(ZRST,"Off") menu item operator sees
        field(ONVL,”0x5") BIT MAP: 0000000000000101 -> do LNK1, LNK3
        field(ONST,"On)") menu item operator sees
        field(TWVL,"0xc") BIT MAP: 0000000000001100 -> do LNK3, LNK4
        field(TWST,"Set @ Default") menu item operator sees
}
record(seq,"$(user):PS:ControlSQ") {
        field(SELM,"Mask")
        field(SELL,"$(user):PS:Control.RVAL NPP NMS")
        field(DLY1,"0")
        field(DOL1,"0")
        field(LNK1,"$(user):PS:setCurrent.VAL PP NMS")
        field(DLY2,"2")
        field(DOL2,"0")
        field(LNK2,"$(user):PS:pwrControl.VAL PP NMS")
        field(DLY3,"0")
        field(DOL3,"1")
        field(LNK3,"$(user):PS:pwrControl.VAL PP NMS")
        field(DLY4,"1")
        field(DOL4,"3.75")
        field(LNK4,"$(user):PS:setCurrent.VAL PP NMS)
}
Off
On
Set @ Default
Different links in the sequence record are executed for each selection of the mbbo. This allows much functionality to be specified in only two records.

---
Database Examples
Automatic Shutdown on Logout
If no CA monitor exists on the SUB record (i.e. the operator logs out), MLIS will be NULL. The subroutine will then set the .VAL field to 0, causing the sequence record to process.

---
Database Examples
Quick Prototyping with Standard Records
Custom Record Definition
Left BPM Button
.INPL
.XPOS
BPM Record
Right BPM Button
.YPOS
.INPR
- Average inputs
- Input history
- Standard deviation
...
.INT
Top BPM Button
.INPT
.VAL
Bottom BPM Button
.INPB