Writing Device Support
Introduction to Device Support
Eric Norum

---
Writing Device Support – Scope
Writing Device Support – Scope
- An overview of the concepts associated with writing EPICS Device Support routines.
- Examples show the “stone knives and bearskins” approach.
- The ASYN package provides a framework which makes writing device support much easier.
  - The concepts presented here still apply.

---
Writing Device Support – Outline
Writing Device Support – Outline
- What is ‘Device Support’?
- The .dbd file entry
- The driver DSET
- Device addresses
- Support routines
- Using interrupts
- Asynchronous input/output
- Callbacks

---
What is ‘Device Support’?
What is ‘Device Support’?
- Interface between record and hardware
- A set of routines for record support to call
  - The record type determines the required set of routines
  - These routines have full read/write access to any record field
- Determines synchronous/asynchronous nature of record
- Performs record I/O
  - Provides interrupt handling mechanism

---
Why use device support?
Why use device support?
- Could instead make a different record type for each hardware interface, with fields to allow full control over the provided facilities.
- A separate device support level provides several advantages:
  - Users need not learn a new record type for each type of device
  - Increases modularity
    - I/O hardware changes are less disruptive
    - Device support is simpler than record support
    - Hardware interface code is isolated from record API
- Custom records are available if really needed.
  - By which I mean “really, really, really needed!”
  - Existing record types are sufficient for most applications.

---
How does a record find its device support?
How does a record find its device support?
Through .dbd ‘device’ statements:

---
The .dbd file entry
The .dbd file entry
The IOC discovers device support from entries in .dbd files
  device(recType,addrType,dsetName,”dtypeName”)
addrType is one of
  AB_IO	BITBUS_IO	CAMAC_IO	GPIB_IO
  INST_IO	RF_IO	VME_IO	VXI_IO
dsetName is the name of the C Device Support Entry Table (DSET)
  - By convention name indicates record and hardware type:
  device(ai, GPIB_IO, devAidg535, "dg535")
  device(bi, VME_IO, devBiXy240, "XYCOM-240")
[Speaker Notes: This is where the actual control and data acquisition occurs.]

---
The DSET
The DSET
- A C structure containing pointers to functions
- Content dependent upon record type
- Each device support layer defines a DSET with pointers to its own functions
- A DSET structure declaration looks like:
  struct dset {
  long number;
  long (*report)(int level);
  long (*initialize)(int pass);
  long (*initRecord)(struct … *precord);
  long (*getIoIntInfo)(…);
  … read/write and other routines as required
  };
- number specifies number of pointers (often 5 or 6)
- A NULL is given when an optional routine is not implemented
- DSET structures and functions are usually declared static

---
The DSET – initialize
The DSET – initialize
long initialize(int pass);
- Initializes the device support layer
- Optional routine, not always needed
- Used for one-time startup operations:
  - Start background tasks
  - Create shared tables
- Called twice by iocInit()
  - pass=0 – Before any record initialization
    Doesn’t usually access hardware since device address information is not yet known
  - pass=1 – After all record initialization
    Can be used as a final startup step. All device address information is now known

---
The DSET – initRecord
The DSET – initRecord
long initRecord(struct … *precord);
- Called by iocInit() once for each record with matching DTYP
- Optional routine, but usually supplied
- Routines often
  - Validate the INP or OUTP field
  - Verify that addressed hardware is present
  - Allocate device-specific storage for the record
    - Each record contains a void *dpvt pointer for this purpose
  - Program device registers
  - Set record-specific fields needed for conversion to/from engineering units

---
The DSET – read/write
The DSET – read/write
long read(struct … *precord);
long write(struct … *precord);
- Called when record is processed
- Perform (or initiate) the I/O operation:
  - Synchronous input
    - Copy value from hardware into precord->rval
    - Return 0 (to indicate success)
  - Synchronous output
    - Copy value from precord->rval to hardware
    - Return 0 (to indicate success)

---
The DSET – initRecord – Device Addresses
The DSET – initRecord – Device Addresses
Device support .dbd entry was
  device(recType,addrType,dset,"name")
addrType specifies the type to use for the address link, e.g.
  device(bo,VME_IO,devBoXy240,"Xycom XY240")
sets pbo->out:
  - pbo->out.type = VME_IO
  - Device support uses pbo->out.value.vmeio which is a
    struct vmeio {
    short card;
    short signal;
    char *parm;
    };
IOC Application Developer’s Guide describes all types

---
A simple example (vxWorks or RTEMS)
A simple example (vxWorks or RTEMS)
#include <recGbl.h>
#include <devSup.h>
#include <devLib.h>
#include <biRecord.h>
#include <epicsExport.h>
static long initRecord(struct biRecord *prec){
char *pbyte, dummy;
if ((prec->inp.type != VME_IO) ||
(prec->inp.value.vmeio.signal < 0) || (prec->inp.value.vmeio.signal > 7)) {
recGblRecordError(S_dev_badInpType, (void *)prec, "devBiFirst: Bad INP");
return -1;
}
if (devRegisterAddress("devBiFirst", atVMEA16, prec->inp.value.vmeio.card, 0x1,
&pbyte) != 0) {
recGblRecordError(S_dev_badCard, (void *)prec, "devBiFirst: Bad VME address");
return -1;
}
if (devReadProbe(1, pbyte, &dummy) < 0) {
recGblRecordError(S_dev_badCard, (void *)prec, "devBiFirst: Nothing there!");
return -1;
}
prec->dpvt = pbyte;
prec->mask = 1 << prec->inp.value.vmeio.signal;
return 0;
}

---
A simple example (vxWorks or RTEMS)
static long read(struct biRecord *prec)
{
volatile char *pbyte = (volatile char *)prec->dpvt;
prec->rval = *pbyte;
return 0;
}
static struct {
long number;
long (*report)(int);
long (*initialize)(int);
long (*initRecord)(struct biRecord *);
long (*getIoIntInfo)();
long (*read)(struct biRecord *);
} devBiFirst = {
5, NULL, NULL, initRecord, NULL, read
};
epicsExportAddress(dset,devBiFirst);

---
The DSET – report
The DSET – report
long report(int level);
- Called by dbior shell command
- Prints information about current state, hardware status, I/O statistics, etc.
- Amount of output is controlled by the level argument
  - level=0 – list hardware connected, one device per line
  - level>0 – provide different type or more detailed information

---
A simple example – device support .dbd file
A simple example – device support .dbd file
The .dbd file for the device support routines shown on the preceding pages might be
device(bi, VME_IO, devBiFirst, “simpleInput”)

---
A simple example – application .db file
A simple example – application .db file
An application .db file using the device support routines shown on the preceding pages might contain
record(bi, "$(P):statusBit")
{
field(DESC, "Simple example binary input")
field(DTYP, "simpleInput")
field(INP, "#C$(C) S$(S)")
}

---
A simple example – application startup script
A simple example – application startup script
An application startup script (st.cmd) using the device support routines shown on the preceding pages might contain
dbLoadRecords("db/example.db","P=test,C=0x1E0,S=0")
which would expand the .db file into
record(bi, "test:statusBit")
{
field(DESC, "Simple example binary input")
field(DTYP, "simpleInput")
field(INP, "#C0x1E0 S0")
}

---
Useful facilities
Useful facilities
- ANSI C routines (EPICS headers fill in vendor holes)
  - epicsStdio.h – printf, sscanf, epicsSnprintf
  - epicsString.h – strcpy, memcpy, epicsStrDup
  - epicsStdlib.h – getenv, abs, epicsScanDouble
- OS-independent hardware access (devLib.h)
  - Bus address → Local address conversion
  - Interrupt control
  - Bus probing
- EPICS routines
  - epicsEvent.h – process synchronization semaphore
  - epicsMutex.h – mutual-exclusion semaphore
  - epicsThread.h – multithreading support
  - recGbl.h – record error and alarm reporting

---
Device interrupts
Device interrupts
- vxWorks/RTEMS interrupt handlers can be written in C
- VME interrupts have two parameters
  - Interrupt level (1-7, but don’t use level 7 on M68k) – often set with on-board jumpers or DIP switches
  - Interrupt vector (0-255, <64 reserved on MC680x0) – often set by writing to an on-board register
OS initialization takes two calls
  - Connect interrupt handler to vector
    devConnectInterruptVME(unsigned vectorNumber,
    void (*pFunction)(void *),void *parameter);
  - Enable interrupt from VME to CPU
    devEnableInterruptLevelVME (unsigned level);

---
I/O interrupt record processing
I/O interrupt record processing
- Record is processed when hardware interrupt occurs
- Granularity depends on device support and hardware
  - Interrupt per-channel vs. interrupt per-card
- #include <dbScan.h> to get additional declarations
- Call scanIoInit once for each interrupt source to initialize a local value:
  scanIoInit(&ioscanpvt);
- DSET must provide a getIoIntInfo routine to specify the interrupt source associated with a record – a single interrupt source can be associated with more than one record
- Interrupt handler calls scanIoRequest with the ‘ioscanpvt’ value for that source – this is one of the very few routines which may be called from an interrupt handler

---
The DSET – getIoIntInfo
The DSET – getIoIntInfo
long getIoIntInfo(int cmd, struct … *precord, IOSCANPVT *ppvt);
- Set *ppvt to the value of the IOSCANPVT variable for the interrupt source to be associated with this record
- You may call scanIoInit to initialize the IOSCANPVT variable if you haven’t done so already
- Return 0 to indicate success or non-zero to indicate failure – in which case the record SCAN field will be set to Passive
- Routine is called with
  - (cmd=0) when record is set to SCAN=I/O Intr
  - (cmd=1) when record SCAN field is set to any other value

---
The DSET – specialLinconv
The DSET – specialLinconv
long specialLinconv(struct … *precord, int after);
- Analog input (ai) and output (ao) record DSETs include this sixth routine
- Called just before (after=0) and just after (after=1) the value of the LINR, EGUL or EGUF fields changes
- “Before” usually does nothing
- “After” recalculates ESLO from EGUL/EGUF and the hardware range if LINR is LINEAR. Doesn’t change ESLO if LINR is SLOPE.
- If LINR field is appropriate ai record processing will compute val as
  val = ((rval + roff) * aslo + aoff) * eslo + eoff
  Ao record processing is similar, but in reverse

---
Asynchronous I/O
Asynchronous I/O
- Device support must not wait for slow I/O
- Hardware read/write operations which take “a long time” to complete must use asynchronous record processing
  - TI/O > 50 µs	– definitely “a long time”
  - TI/O < 2 µs	– definitely “not a long time”
  - 2 µs < TI/O < 50 µs	– ???
- If device does not provide a completion interrupt a “worker” thread can be created to perform the I/O
  - this technique is used for message-based (GPIB, USB, Serial, Ethernet) devices

---
Asynchronous I/O – read/write operation
Asynchronous I/O – read/write operation
- Check value of precord->pact and if zero:
  - Set precord->pact to 1
  - Start the I/O operation
    - write hardware or send message to worker thread
  - Return 0
- When operation completes run the following code from a thread (i.e. NOT from an interrupt handler)
  struct rset *prset = (struct rset *)precord->rset;
  dbScanLock(precord);
  (*prset->process)(precord);
  dbScanUnlock(precord);
The record’s process routine will call the device support read/write routine – with precord->pact=1
  - Complete the I/O, set rval, etc.

---
Asynchronous I/O – callbacks
Asynchronous I/O – callbacks
- An interrupt handler must not call a record’s process routine directly
- Use the callback system (callback.h) to do this
- Declare a callback variable
  CALLBACK myCallback;
Issue the following from the interrupt handler
  callbackRequestProcessCallback(&myCallBack,priorityLow,precord);
- This queues a request to a callback handler thread which will perform the lock/process/unlock operations shown on the previous page
- There are three callback handler threads
  - With priorities Low, Medium and High

---
Asynchronous I/O – ASYN
The ASYN Support Module
- This should be your first consideration for new device support
- It provides a powerful, flexible framework for writing device support for
  - Message-based asynchronous devices
    - In many cases these can be supported with no C programming at all (ASYN+StreamDevice)
  - Register-based synchronous devices