Enhancements to motor record device and driver support
Peter Denison
Diamond Light Source

---
Contents
Recap of Aims
Architecture
Example
Progress
Future
[Speaker Notes: This follows on from the talk given at Archamps in Oct 2005]

---
Recap of Aims
Simpler to write motor controller driver
Extensible API
Allow trivial use with standard records in base
Start with support for OMS, PMAC, MM4000
[Speaker Notes: As the talk in October outlined, the main aim was to tidy up the existing motor record drivers, making the task of writing a new one easier. We also want to be able to use the drivers with other records, and to have an interface that will support new features in the future, so we don't have to do this process again The motor record is a commonly used interface, and we want to preserve that interface.]

---
Architecture
Single device support for motor record
Single Asyn-compatible driver interface layer
Multiple drivers
  - separate modules
  - accessed by drvet name
[Speaker Notes: The drivers export a name, and this is used by the upper layers to get at the interface. This provides run-time linkage, not compile-time linkage]

---
Layers
Ethernet
RS232
devMotorAsyn
devAsynFloat64
drvMotorPMAC
drvMotorXPS
MotorAPI
drvMotorAsyn
XPS
XPS
drvAsynIPPort
drvAsynSerialPort
XPS Controller
PMAC Controller
= Asyn Port
devMotorAsyn
PMAC
[Speaker Notes: We have extracted a set of “Motor Primitives”, and wrapped them in the MotorAPI interface. Note the change to the DTYP and OUT fields of the motor records. Whilst we are keeping the behaviour and interface to the motor record the same, there have to be some minor changes to the Dbs to use the new style. Code for devMotorAsyn is common Code for drvMotorAsyn is common Boxes in blue are all you have to write for a new motor controller driver]

---
Startup
### XPS Set Up
# cards (total controllers), scan rate
XPSSetup(2)
#
# card, IP, PORT, number of axes, active poll period (ms), idle poll period (ms)
XPSConfig(0, "172.23.116.160", 5001, 2, 10, 500)
# asyn port, driver name, controller index, max. axes)
drvAsynMotorConfigure("XPS", "motorXPS", 0, 2)
#
# card, axis, groupName.positionerName
XPSConfigAxis(0,0,"Z1_Z2_Z3.Z1_BASE", 10000)
XPSConfigAxis(0,1,"Z1_Z2_Z3.Z2_BASE", 10000)
Allocate Memory
Setup Controller
Create underlying Asyn port for comms
Create top-level Asyn port for motor primitives
Attach to a driver registered as “motorXPS”
Assign each axis by name to
an Asyn address
(peculiar to this controller)

---
Startup
# Configure the VME carrier card
IPAC4 = ipacEXTAddCarrier(&EXTHy8002, "4 2 192")
# Configure the stepper motor IP card
drvHy8601Configure(40, IPAC4, 0, 193, 0, 0)
# Setup the motor Asyn layer (portname, low-level driver drvet name, card, number of axes on card, can_block)
drvAsynMotorConfigure("MOTOR", "drvHy8601Asyn", 40, 4, 0)
[Speaker Notes: Much simpler example The card has 4 axes, and is configured in a similar way to other IP modules Then, the Asyn motor port is created on top to handle motor primitives]

---
Startup
# Configure the VME card addresses
pmacVmeConfig (0, 0x7FA000, 0x700000, 0xc1, 2)
# Create the DRPAM ASCII buffer serial driver /dev/pmac/*/asc
pmacDrv()
# Setup the underlying Asyn port for comms
drvAsynSerialPortConfigure("p0", "/dev/pmac/0/asc",0,0,0 )
# Create axes communicating via Asyn port “PMAC”, addr 0
# on card 0, 6 axes
pmacAsynMotorCreate("p0", 0, 0, 6 )
# Setup the motor Asyn layer (portname, low-level driver drvet name, card, number of axes on card)
drvAsynMotorConfigure("PMAC", "pmacAsynMotor", 0, 6)

---
Progress
Common device support for motor record
Common Asyn driver interface layer
Simulated motor written to help testing
  - both 'old-style' and Asyn dev support
Support for 3 controllers
  - 2 more under development
Pre-release part of motor R5-9

---
Layers (2)
?
motorRecord
devMotorAsyn
new API
Coordinated motion
Record?
Controller specific
programming?
drvMotorAsyn
Interposed Interface
?
Underlying Asyn Port
[Speaker Notes: New records (or some existing ones) could support coordinated motion Controller specific parameters such as compensation tables or coordinate transformations could be supported by extending the API]

---
Future
Lots more testing
Profiled moves
Coordinated motion?
Extending interfaces
Convert more controllers – do you want it?

---
Thank you
Nick Rees, Diamond – new API, Sim, PMAC
Mark Rivers, APS / CARS – MM4000, XPS
Ron Sluiter, APS – OMS
[Speaker Notes: This project is, as many others, a collaboration Email addresses: peter.denison@diamond.ac.uk nick.rees@diamond.ac.uk rivers@cars.uchicago.edu sluiter@aps.anl.gov]