## Slide 1: Managing IOCs with Local Filesystems
Scott A. Baily
Eric Björklund
10/05/2013

## Slide 2: New trends: Many more IOCs; Readily available flash memory.
Our upgrade path will result in an order of magnitude more IOCs.
It is no longer acceptable to walk the accelerator pressing reset buttons after a site-wide power outage.
The flash memory available or already included with new IOCs, provides a solution.

## Slide 3: IOCs that boot from NFS have features we should preserve
Changes are made on the NFS server, and take effect at the next boot.
The IOC does not have to be reachable to make changes.
Autosave files are still available for use by a spare IOC in the event of hardware failure.
Pull from server is more robust than push.

## Slide 4: Disadvantages of IOCs that boot from NFS
The IOC cannot boot if the network or the NFS server is down.
If the NFS server is unreachable the IOC gets stuck.
If a reboot occurs while rebuilding files, the IOC can get stuck.
Autosave files can’t be saved while the network is down.

## Slide 5: Plan: IOCs sync with server, but boot from the local filesystem
A very simple local startup script
  Loads the kernel
  Mounts the NFS server
  Copies the IOC specific startup script.
Files are copied by the script that uses them
  The first script doesn’t need the entire list.
Autosave .sav files are stored locally, but periodically copied to the NFS server.

## Slide 6: A few simple utilities needed
cpnew (the equivalent of “cp –u” on linux)
  Can’t use EPICS OSI.
  Uses only POSIX functions.
  Newer files must be at least 3 seconds newer
    FAT32 files systems have low timestamp precision
cpsys (Also reboots the IOC if files are copied)
  Used for kernel updates.
Periodic backup tool

## Slide 7: Periodic backup tool: Updates NFS server with local data files
Autosave itself can almost perform this function with a periodic backup set.
  Autosave will recover from stale NFS handles, but does not mount the server if it has never been mounted.
  A separate location for the periodic backup set can only be specified after IOC start.

## Slide 8: Disadvantages
Requires multiple reboots if the kernel needs to be updated.
If new IOC is installed, one must be careful if files are installed using a tool that doesn’t preserve the original file date.
  Some drive imaging tools use the current date
    if an old image is used it should exclude most of the files managed by these tools.
    One must also verify that the latest kernel is included in the image.

## Slide 9: Best of both worlds
IOCs pull their own files at boot.
Most boots are faster as only the filenames and timestamps are sent over the network.
IOCs are fully functional if the NFS server is down, or if the network was down at boot.
Missing files on the server (during a rebuild) don’t result in a stuck IOC.
Autosave .sav files are available for spares