If the oxygen deficiency alarm goes off, and either of the Automatic LN2 Fill Stations seem to be malfunctioning (not closing) it may be necessary to remotely secure the power and/or LN2 supply to the auto fill stations. There is only one power supply and LN2 supply for each pair of fill stations.

|  |  |  |  |
| --- | --- | --- | --- |
| **Truck Lock** | **Power Supply Breaker Location** | **Isolation** **Valve Location** | **Note** |
| **431-432** | **RP-M1-432, Circuit 5.**432A Corridor outside A020 | Outside, on top of the pad between the storage tanks.  |  |
| **433-434** | **RP-M1-434, Circuit 5.**434A inside lab A020. | On the opposite side of the wall from where the piping enters the truck-lock. | Closing this LN2 supply valve will close off ALL the LN2 supply to Module B. **Sectors 10 to 17 WILL LOSE THEIR SUPPLY OF LN2**. If this valve is closed for emergency purposes, **contact the MCR Immediately,** and have an interconnect valve to an adjacent module opened.  |
| **435-436** | **RP-M7-435, Circuit 4.**435E Corridor outside E020 | On the opposite side of the wall from where the piping enters the truck-lock. |  |
| **437-438** | **RP-M1-438, Circuit 5.**438A Corridor outside A020 | On the opposite side of the wall from where the piping enters the truck-lock. | Closing this LN2 supply valve will close off ALL the LN2 supply to Module D. **Sectors 28 to 35 WILL LOSE THEIR SUPPLY OF LN2**. If this valve is closed for emergency purposes, **contact the MCR Immediately,** and have an interconnect valve to an adjacent module opened.  |